## Sheet1
|  |  | User ID | : | 1
|  |  | Cal. ID | : | 334
|  |  | Date | : | 2023-09-01 18:29
Product Information
| Series | ES
| Model | ESU25AES
| Flow Configuration | BOT INTAKE - TOP DISC
| Refrigerant | R410A
| Unit Dimension LxDxH | 800 x 891 x 1985 mm³
| Power Supply | 400V-3ph-50Hz
Fan Information
| Fan Type | AC 500 D
| No. of Fan | 1
| Fan Speed | 1302 RPM
| Filter Type | G4
| Airflow Rate | 6630 m³/hr
| External Static Pressure | 50 Pa
| Total Static Pressure | 320 Pa
| Motor Heat | 0.88 kW
Entering Air Properties
| Dry Bulb Temperature | 22.0 °C
| Relative Humidity | 45.0 %
| Wet Bulb Temperature | 14.7 °C
Outlet Air Properties
| Dry Bulb Temperature | 11.6 °C
| Relative Humidity | 83.3 %
| Wet Bulb Temperature | 10.1 °C
Refrigeration System/Circuit
| Ambient Temperature | 35.0 °C
| No. of Circuit | 1
| Condenser Model | HEC314
| Heat Rejection | 30.22 kW
| Compressor Size | 8HP
| Evaporating Temperature | 6.1 °C
| Condensing Temperature | 6.6 kW
Compressor Power Input
Unit Capacity
| Gross Total Capacity | 23.62 kW
| Gross Sensible Capacity | 21.75 kW
| Gross SHR | 0.92
| Net Total Capacity | 22.74 kW
| Net Sensible Capacity | 20.87 kW
| Net SHR | 0.92