## Sheet1
|  |  | User ID | : | 1
|  |  | Cal. ID | : | 370
|  |  | Date | : | 2024-01-04 14:02
Product Information
| Series | EV
| Model | EZU2090AS5
| Flow Configuration | BOT INTAKE - TOP DISC
| Refrigerant | R410A
| Unit Dimension LxDxH | 2500 x 891 x 1985 mm³
| Power Supply | 400V-3ph-50Hz
Fan Information
| Fan Type | EC 560 D
| No. of Fan | 2
| Fan Speed | 1671 RPM
| Filter Type | G4
| Airflow Rate | 25920 m³/hr
| External Static Pressure | 50 Pa
| Total Static Pressure | 425 Pa
| Motor Heat | 2.48 kW
Entering Air Properties
| Dry Bulb Temperature | 24.0 °C
| Relative Humidity | 45.0 %
| Wet Bulb Temperature | 16.3 °C
Outlet Air Properties
| Dry Bulb Temperature | 14.0 °C
| Relative Humidity | 81.2 %
| Wet Bulb Temperature | 12.2 °C
Refrigeration System/Circuit
| Ambient Temperature | 35.0 °C
| No. of Circuit | 2
| Condenser Model | HEC654
| Heat Rejection | 60.64 kW
| Compressor Size | 15HP
| Evaporating Temperature | 8.2 °C
| Condensing Temperature | 13.2 kW
Compressor Power Input
Unit Capacity
| Gross Total Capacity | 94.88 kW
| Gross Sensible Capacity | 88.56 kW
| Gross SHR | 0.93
| Net Total Capacity | 92.4 kW
| Net Sensible Capacity | 86.08 kW
| Net SHR | 0.93