## Sheet1
|  |  | User ID | : | 1
|  |  | Cal. ID | : | 373
|  |  | Date | : | 2024-01-05 15:00
Product Information
| Series | EZ
| Model | EZU1020AS5
| Flow Configuration | BOT INTAKE - TOP DISC
| Refrigerant | R410A
| Unit Dimension LxDxH | 800 x 891 x 1985 mm³
| Power Supply | 400V-3ph-50Hz
Fan Information
| Fan Type | EC 500 D
| No. of Fan | 1
| Fan Speed | 1302 RPM
| Filter Type | G4
| Airflow Rate | 6630 m³/hr
| External Static Pressure | 50 Pa
| Total Static Pressure | 320 Pa
| Motor Heat | 0.88 kW
Entering Air Properties
| Dry Bulb Temperature | 24.0 °C
| Relative Humidity | 45.0 %
| Wet Bulb Temperature | 16.3 °C
Outlet Air Properties
| Dry Bulb Temperature | 15.2 °C
| Relative Humidity | 77.8 %
| Wet Bulb Temperature | 12.9 °C
Refrigeration System/Circuit
| Ambient Temperature | 35.0 °C
| No. of Circuit | 1
| Condenser Model | HEC274
| Heat Rejection | 25.23 kW
| Compressor Size | 6HP
| Evaporating Temperature | 9.7 °C
| Condensing Temperature | 5.0 kW
Compressor Power Input
Unit Capacity
| Gross Total Capacity | 20.23 kW
| Gross Sensible Capacity | 20.23 kW
| Gross SHR | 1.0
| Net Total Capacity | 19.35 kW
| Net Sensible Capacity | 19.35 kW
| Net SHR | 1.0