## Sheet1
|  |  | User ID | : | 1
|  |  | Cal. ID | : | 339
|  |  | Date | : | 2023-09-27 14:38
Product Information
| Series | EZ
| Model | EZU1030AS5
| Flow Configuration | BOT INTAKE - TOP DISC
| Refrigerant | R410A
| Unit Dimension LxDxH | 885 x 891 x 1985 mm³
| Power Supply | 400V-3ph-50Hz
Fan Information
| Fan Type | EC 500 D
| No. of Fan | 1
| Fan Speed | 1428 RPM
| Filter Type | G4
| Airflow Rate | 8070 m³/hr
| External Static Pressure | 50 Pa
| Total Static Pressure | 333 Pa
| Motor Heat | 1.15 kW
Entering Air Properties
| Dry Bulb Temperature | 24.0 °C
| Relative Humidity | 45.0 %
| Wet Bulb Temperature | 16.3 °C
Outlet Air Properties
| Dry Bulb Temperature | 13.8 °C
| Relative Humidity | 82.1 %
| Wet Bulb Temperature | 12.1 °C
Refrigeration System/Circuit
| Ambient Temperature | 35.0 °C
| No. of Circuit | 1
| Condenser Model | HEC374
| Heat Rejection | 36.66 kW
| Compressor Size | 10HP
| Evaporating Temperature | 8.1 °C
| Condensing Temperature | 7.7 kW
Compressor Power Input
Unit Capacity
| Gross Total Capacity | 28.96 kW
| Gross Sensible Capacity | 26.8 kW
| Gross SHR | 0.93
| Net Total Capacity | 27.81 kW
| Net Sensible Capacity | 25.65 kW
| Net SHR | 0.92