## Sheet1
|  |  | User ID | : | 1
|  |  | Cal. ID | : | 340
|  |  | Date | : | 2023-09-29 15:10
Product Information
| Series | ESM
| Model | ESMU08AS5
| Flow Configuration | BOT INTAKE - TOP DISC
| Refrigerant | R410A
| Unit Dimension LxDxH | 650 x 655 x 1940 mm³
| Power Supply | 400V-3ph-50Hz
Fan Information
| Fan Type | AC 400 D
| No. of Fan | 1
| Fan Speed | 1370 RPM
| Filter Type | G4
| Airflow Rate | 2980 m³/hr
| External Static Pressure | 184 Pa
| Total Static Pressure | 321 Pa
| Motor Heat | 0.51 kW
Entering Air Properties
| Dry Bulb Temperature | 24.0 °C
| Relative Humidity | 45.0 %
| Wet Bulb Temperature | 16.3 °C
Outlet Air Properties
| Dry Bulb Temperature | 14.3 °C
| Relative Humidity | 76.7 %
| Wet Bulb Temperature | 12.0 °C
Refrigeration System/Circuit
| Ambient Temperature | 35.0 °C
| No. of Circuit | 1
| Condenser Model | HEC274
| Heat Rejection | 13.38 kW
| Compressor Size | 4HP
| Evaporating Temperature | 7.1 °C
| Condensing Temperature | 2.4 kW
Compressor Power Input
Unit Capacity
| Gross Total Capacity | 10.98 kW
| Gross Sensible Capacity | 9.6 kW
| Gross SHR | 0.87
| Net Total Capacity | 10.47 kW
| Net Sensible Capacity | 9.09 kW
| Net SHR | 0.87