## Sheet1
|  |  | User ID | : | 1
|  |  | Cal. ID | : | 375
|  |  | Date | : | 2024-02-19 12:44
Product Information
| Series | EV
| Model | EVU2070AS5
| Flow Configuration | BOT INTAKE - TOP DISC
| Refrigerant | R410A
| Unit Dimension LxDxH | 1815 x 891 x 1985 mm³
| Power Supply | 400V-3ph-50Hz
Fan Information
| Fan Type | EC 500 D
| No. of Fan | 2
| Fan Speed | 1652 RPM
| Filter Type | G4
| Airflow Rate | 19080 m³/hr
| External Static Pressure | 50 Pa
| Total Static Pressure | 440 Pa
| Motor Heat | 1.82 kW
Entering Air Properties
| Dry Bulb Temperature | 24.0 °C
| Relative Humidity | 45.0 %
| Wet Bulb Temperature | 16.3 °C
Outlet Air Properties
| Dry Bulb Temperature | 13.1 °C
| Relative Humidity | 83.0 %
| Wet Bulb Temperature | 11.5 °C
Refrigeration System/Circuit
| Ambient Temperature | 35.0 °C
| No. of Circuit | 2
| Condenser Model | HEC574
| Heat Rejection | 50.4 kW
| Compressor Size | 5HP
| Evaporating Temperature | 7.3 °C
| Condensing Temperature | 10.8 kW
Compressor Power Input
Unit Capacity
| Gross Total Capacity | 79.2 kW
| Gross Sensible Capacity | 70.45 kW
| Gross SHR | 0.89
| Net Total Capacity | 77.38 kW
| Net Sensible Capacity | 68.63 kW
| Net SHR | 0.89