## Sheet1
|  |  | User ID | : | 1
|  |  | Cal. ID | : | 378
|  |  | Date | : | 2024-01-08 11:54
Product Information
| Series | ESM
| Model | ESMU10AS5
| Flow Configuration | BOT INTAKE - TOP DISC
| Refrigerant | R410A
| Unit Dimension LxDxH | 650 x 655 x 1940 mm³
| Power Supply | 400V-3ph-50Hz
Fan Information
| Fan Type | AC 400 D
| No. of Fan | 1
| Fan Speed | 1370 RPM
| Filter Type | G4
| Airflow Rate | 2990 m³/hr
| External Static Pressure | 181 Pa
| Total Static Pressure | 319 Pa
| Motor Heat | 0.51 kW
Entering Air Properties
| Dry Bulb Temperature | 24.0 °C
| Relative Humidity | 45.0 %
| Wet Bulb Temperature | 16.3 °C
Outlet Air Properties
| Dry Bulb Temperature | 14.9 °C
| Relative Humidity | 75.3 %
| Wet Bulb Temperature | 12.4 °C
Refrigeration System/Circuit
| Ambient Temperature | 35.0 °C
| No. of Circuit | 1
| Condenser Model | HCC184
| Heat Rejection | 13.18 kW
| Compressor Size | 4HP
| Evaporating Temperature | 7.6 °C
| Condensing Temperature | 2.7 kW
Compressor Power Input
Unit Capacity
| Gross Total Capacity | 10.48 kW
| Gross Sensible Capacity | 9.48 kW
| Gross SHR | 0.9
| Net Total Capacity | 9.97 kW
| Net Sensible Capacity | 8.97 kW
| Net SHR | 0.9