## Sheet1
|  |  | User ID | : | 1
|  |  | Cal. ID | : | 379
|  |  | Date | : | 2024-01-08 11:54
Product Information
| Series | ESM
| Model | ESMU20AS5
| Flow Configuration | BOT INTAKE - TOP DISC
| Refrigerant | R410A
| Unit Dimension LxDxH | 800 x 890 x 1985 mm³
| Power Supply | 400V-3ph-50Hz
Fan Information
| Fan Type | AC 450 D
| No. of Fan | 1
| Fan Speed | 1400 RPM
| Filter Type | G4
| Airflow Rate | 4890 m³/hr
| External Static Pressure | 184 Pa
| Total Static Pressure | 352 Pa
| Motor Heat | 1.1 kW
Entering Air Properties
| Dry Bulb Temperature | 25.0 °C
| Relative Humidity | 45.0 %
| Wet Bulb Temperature | 17.1 °C
Outlet Air Properties
| Dry Bulb Temperature | 14.0 °C
| Relative Humidity | 84.9 %
| Wet Bulb Temperature | 12.5 °C
Refrigeration System/Circuit
| Ambient Temperature | 35.0 °C
| No. of Circuit | 1
| Condenser Model | HCC244
| Heat Rejection | 26.36 kW
| Compressor Size | 6HP
| Evaporating Temperature | 8.8 °C
| Condensing Temperature | 5.8 kW
Compressor Power Input
Unit Capacity
| Gross Total Capacity | 20.56 kW
| Gross Sensible Capacity | 18.87 kW
| Gross SHR | 0.92
| Net Total Capacity | 19.46 kW
| Net Sensible Capacity | 17.77 kW
| Net SHR | 0.91