## Sheet1
|  |  | User ID | : | 1
|  |  | Cal. ID | : | 380
|  |  | Date | : | 2024-01-08 11:54
Product Information
| Series | EV
| Model | EZU2070AS5
| Flow Configuration | BOT INTAKE - TOP DISC
| Refrigerant | R410A
| Unit Dimension LxDxH | 1815 x 891 x 1985 mm³
| Power Supply | 400V-3ph-50Hz
Fan Information
| Fan Type | EC 500 D
| No. of Fan | 2
| Fan Speed | 1796 RPM
| Filter Type | G4
| Airflow Rate | 20780 m³/hr
| External Static Pressure | 50 Pa
| Total Static Pressure | 513 Pa
| Motor Heat | 2.33 kW
Entering Air Properties
| Dry Bulb Temperature | 25.0 °C
| Relative Humidity | 42.0 %
| Wet Bulb Temperature | 16.5 °C
Outlet Air Properties
| Dry Bulb Temperature | 14.5 °C
| Relative Humidity | 80.4 %
| Wet Bulb Temperature | 12.6 °C
Refrigeration System/Circuit
| Ambient Temperature | 35.0 °C
| No. of Circuit | 2
| Condenser Model | HEC574
| Heat Rejection | 46.36 kW
| Compressor Size | 13HP
| Evaporating Temperature | 8.7 °C
| Condensing Temperature | 9.2 kW
Compressor Power Input
Unit Capacity
| Gross Total Capacity | 74.31 kW
| Gross Sensible Capacity | 74.31 kW
| Gross SHR | 1.0
| Net Total Capacity | 71.98 kW
| Net Sensible Capacity | 71.98 kW
| Net SHR | 1.0